## 3-Phase
TECHNICAL SPECIFICATION OF 3-Phase UPS SERIES
PHASE |  | 3-Phase Input / 3-Phase Output | [11 empty] | 3-Phase Input / 1-Phase Output
KVA |  | 10 | 20 | 30 | 40 | 50 | 60 | 80 | 100 | 120 | 160 | 240 | 320 | 10 | 20 | 30 | 40 | 50
INPUT (RECTIFIER)
Input Voltage |  | 220VΔ / 380VΔ / 460VΔ, 208VY / 380VY / 400VY / 415VY
Input Range |  | + / - 20% ( > +/- 20% is available upon request)
Input Frequency |  | 50 / 60 Hz + / - 5Hz
Power Walk In |  | 0% - 100% : 20 sec
Efficiency |  | ≒ 98%
Voltage Regulation |  | + / - 1%
BATTERY
Battery Type / Pcs |  | Maintenance free lead-acid batteries / 12V x 29pcs
Maximum Charge Current Adc (Selectable) |  | 5 | 10 | 15 | 20 | 25 | 30 | 40 | 50 | 60 | 80 | 120 | 160 | 5 | 10 | 15 | 20 | 25
Battery Start |  | Yes, UPS can be started without AC source.
INVERTER
Output Voltage |  | 220VΔ / 380VΔ / 460VΔ, 208VY / 380VY / 400VY / 415VY, + / - 1 % | [11 empty] | 220 / 230 / 240 V, 1Φ2ωor3ω
Wave Form |  | Sine Wave
Output Power Factor |  | 0.8
Frequency Lock Range |  | 50 / 60 Hz + / - 3Hz
Output Frequency (Free Running) |  | 50 / 60 Hz + / - 0.1 Hz
Phase Shift Under 100% Unbalance Load |  | < 0.5°
THD (Linear Load) |  | < 2 %
Overload | <110% | Continuous
| 110 – 125% | 15 minutes
| 125 – 150% | 10 minutes
| > 150% | 1 minute
Efficiency (100% Load) |  | 93% | 93% | 93% | 93.5% | 93.5% | 94% | 94.5% | 94.5% | 95% | 95% | 95% | 95% | 93% | 93% | 93% | 93.5% | 93.5%
STATIC SWITCH
Voltage Range |  | 173-277 VAC (L-N)
Mains ←→ Inverter |  | 0 ms
OVERALL CHARACTERISTICS
Overall Efficiency |  | 91% | 91% | 91% | 91.5% | 92% | 92% | 92.5% | 92.5% | 93% | 93% | 93% | 93% | 91% | 91% | 91% | 91.5% | 92%
Maximum Heat Dissipation (Kw) |  | 1.1 | 1.3 | 1.9 | 2.6 | 3 | 3.5 | 4.6 | 5.4 | 6.5 | 8.7 | 13 | 17.4 | 1.1 | 1.3 | 1.9 | 2.6 | 3
Height x Width x Depth (mm) |  | 1600 x 550 x 800 | [5 empty] | 80-160KVA: 1600 x 1100 x 800, 240-320KVA: 1600 x 2200 x 800 | [5 empty] | 1600 x 550 x 800
Weight (Kg, without battery) (for standard 380V Y input only) |  | 300 | 350 | 400 | 480 | 550 | 680 | 820 | 950 | 1180 | 1450 | 1950 | 2450 | 300 | 350 | 400 | 480 | 550
Audible Noise |  | < 65 dBA (At 1 M) | [5 empty] | < 67 dBA (At 1 M) | [5 empty] | < 65 dBA (At 1 M)
Temperature |  | 0 – 40℃ ( 32 – 104℉ )
Humidity |  | 0% - 90% (Non–Condensing)
Altitude |  | <1500 M Above Sea Level
EN50091-1,-2 |  | YES
Short Circuit Pretection |  | YES
Lightning / EMC Filter |  | MOV / Input&Output (FCC CLASS A)
Galvanic Isolation |  | Input&Output true Galvanic isolation
LED,LCD,Buzzer |  | YES
Remote Control / Communication Interface |  | Monitoring 1~99 UPS simultaneously / Dry contact, RS232, RS485
☆ Different specifications required are available.
☆ All specifications mentioned above are subject to change without prior notice.