## PG
POWER GUARD LINE INTERACTIVE SINEWAVE UPS SPECIFICATION
■Microprocessor control guarantees high reliability
■Built-in Boost and Buck AVR to stabilize the voltage to our computer
against wide utility voltage fluctuations and brownouts
■Pure Sine Wave Output
■Smart RS-232 Communication Port
■Free download software from www.eeyes.com.tw
■Easy-to-read status indicators and easy-to-use controls with audible
alarms for critical warnings
~ 19" Rack Mount available
■Overload, Short-Circuit, and Overheat Protection
Specification | [5 empty] | Tower type | Rack-mount type
MODEL | Tower type |  | PGA-1000 | PGA-1250 | PGB-2000 | PGB-2500 | PGC-3000 | PGC-3500
| Rack mount type |  | PG2-1000 (2U) | PG2-1250 (2U) | PG3-2000 (3U) | PG3-2500 (3U) | PG4-3000 (4U) | PG4-3500 (4U)
CAPACITY | VA/W |  | 1000VA/600W | 1250VA/750W | 2000VA/1200W | 2500VA/1500W | 3000VA/1800W | 3500VA/2100W
INPUT | Voltage |  | 110VAC / 230VAC
| Voltage Range | Acceptable Voltage Range | 89-129VAC / 178-260VAC
|  | FREQUENCY |  | 47Hz ~ 68Hz, 50Hz / 60Hz (Auto Sensing)
|  | Line Low Transfer | 82VAC ± 4% or 168VAC ± 4%
|  | Line Low Comeback | 89VAC ± 4% or 178VAC ± 4%
|  | Line High Transfer | 136VAC ± 4% or 272VAC ± 4%
|  | Line High Comeback | 129VAC ± 4% or 260VAC ± 4%
OUTPUT | Voltage |  | 110VAC or 230VAC
| Voltage Regulation (Batt. Mode) |  | ±7% RMS for entire battery voltage range
| Frequency |  | 50Hz or 60Hz
| Frequency Regulation (Batt. Mode) |  | ±0.5Hz
| Waveform |  | Pure Sinewave
TRANSFER TIME | Typical |  | 4-6ms
BATTERY | Tower | Battery Type* | 12V/7.2Ah x 2pcs | 12V/8Ah x 2pcs | 12V/7.2Ah x 4pcs | 12V/8Ah x 4pcs | 12V/5Ah x 8pcs | 12V/5Ah x 8pcs
| Rack | Battery Type* | 12V/7.2Ah x 2pcs | 12V/8Ah x 2pcs | 12V/7.2Ah x 4pcs | 12V/8Ah x 4pcs | 12V/5Ah x 8pcs | 12V/5Ah x 8pcs
| Backup Time (at full load) |  | 5-10 minutes (Typical)
| Recharge Time |  | 4 hours to 95% after discharged
INDICATORS | AC Mode |  | Green LED lighting
| Backup Mode |  | Green LED flashing
| Boost/Buck |  | Yellow LED lighting
| Load/Battery Level |  | It represents Load Level in AC Mode and Battery Level in Backup Mode
4-segment LED bar- 0-25% : 4th LED lighting 26%-50% : 3rd and 4th LEDs lighting
51%-75% : 2nd, 3rd, and 4th LEDs lighting
76%-100% : 4 LEDs in a row all lighting
| UPS Fault |  | The 2nd LED in a row of Load/Battery LEDs flashing once every second and one or more addition load/battery level LEDs lighting
| Overload |  | The 1st LED in a row of Load/Battery LEDs flashing once every 0.5 second and all other load/battery level LEDs lighting
| Low Battery |  | The bottom LED in a row of Load/Battery LEDs flashing every 2 seconds
AUDIBLE ALARM | Backup Mode |  | Sounding every 10 seconds
| Low Battery |  | Sounding every 5 seconds
| UPS Fault |  | Continuously Sounding
| Overload |  | Sounding every 0.5 second
| Battery Replacement |  | Sounding 2 seconds every 60 seconds
PHYSICAL | Tower Case | Dimension (DxWxH) mm | 390x125x190 | 390x125x190 | 420x200x290 | 420x200x290 | 460x200x290 | 460x200x290
|  | Net weight (kgs) | 15 | 16 | 25 | 26 | 35 | 36
| Rack Case | Dimension (DxWxH) mm | 375x482x85 | 375x482x85 | 445x482x130 | 445x482x130 | 445x482x172 | 445x482x172
|  | Net weight (kgs) | 16 | 17 | 27 | 28 | 35 | 36
ENVIRONMENT | Operating Environment |  | 0- 40°C, 0-90 % relative humidity (non-condensing)
| Noise Level |  | Less than 45dB
INTERFACE | RS-232 |  | Support Windows 95/98/NT/2000/XP, Novell, and Linux
* Product specifications are subject to change without further notice